## Connections - NLi120Q or NLi120X
### MODBUS RTU only

nl120q_m12_standard.jpg
Nli120Q/X is equipped with two M12 connectors.
For power connector ⇒ power female DA00022011 flying leads and for signal connector ⇒ signal male DA00012011.
da0012011_image.jpg	da00022011_image.jpg
Signal cable DA00012011	Power cable DA0022011 The power cable terminates with two wire: RED (+24VDC), BLACK (GROUND).

The signal cable DA00012011 terminates with with D-SUB15 male connector with this pinout:
D-SUB 15 Pinout	SIGNAL	DESCRIPTION	FUNCTION
1	RS485_B	Modbus B
2	RS485_A	Modbus A
3	GND	Ground
4	NC	Not connected
5	NC	Not connected
6	GND	Ground
7	GND	Ground
8	DIG_IN_0	Digital Input 0 (24V logic)	Enable/Homing
9	DIG_IN_1	Digital Input 1 (24V logic)	Motion trigger
10	DIG_OUT_0	Digital output 0 (24V logic, PNP)	Motor running
11	DIG_OUT_1	Digital output 1 (24V logic, PNP)	Motor fault
12	DIG_OUT_2	Digital output 2 (24V logic, PNP)	Programmable

The programmable output have the following options:
### MODBUS RTU + USB

This model has the same connectors and pinout of the MODBUS RTU only except for the additional USB connector for MODBUS over USB connection.
### CANOPEN, MODBUS RTU and single rear connector

nl120q_s_rear.179.jpg
The hybrid for NLi120Q/X M12 and D-SUB9 connector is DA012019-5M

da012019.jpg
D-SUB9 Pinout	SIGNAL	SIGNAL	WIRE COLOR
1	CAN_H	Canbus high	Brown
2	CAN_L	Canbus LOW	Green
3	MODBUS_A	Modbus A	Yellow
4	MODBUS_B	Modbus B	Grey
5	–	–	–
6	GND	Ground	Violet
7	GND	Ground	Blue
8	24V	Power	White
9	24V	Power	Red

### MODBUS RTU and CANOPEN or ANALOG INPUTS

nl120q_m12_can.jpg
The Can cable for NLi120Q/X (third connector M12 female) and D-SUB9 connector is DA122011

can_cable.jpg
D-SUB9 Pinout	SIGNAL	CAN VERSION	ANALOG VERSION	CAN VERSION WIRE COLOR
1	NC	–	PULSE IN/OUT	-
2	CAN_L	Canbus LOW	DIR IN/OUT	White
3	CAN_GND	Canbus Ground	GND	Yellow/Green or Gray
4	NC	–	-	-
5	NC	–	ANP (0 to 10V voltage control)	-
6	NC	–	ANN (4 to 20mA current control)	-
7	CAN_H	CAN HIGH	-	Brown
8	CAN_RES	TERMINATION RESISTANCE	-	Black
9	CAN_H	CAN HIGH	-	Blue

In order to have the termination on the node, please make a jumper between CAN_RES andf CAN_L (Pin 8 and Pin 2)
### M12 power connector on the motor side pinout

m12_power.jpg
Pin	Signal	Description
1	+24VDC	24VDC power line
2	+24VDC	24VDC power line
3	GND	Ground
4	GND	Ground
5	NC	Not connected